## Fan and Damper
The maintenance for Tunnel Ventilation Equipment is as follows:
A) Tunnel Ventilation Fans and Trackway Exhaust Fan
S. No | Item | Frequency (Months) | Action
1 | Clean the Impeller and blade | 1m | Clean and ensure no build up of dirt or damage to blades - replace or repair blades as appropriate.
2 | Motor Casings cleaning | 1m | Clean dust and entrapment of foreign particles
3 | Motor Lubrication | 3m | Lubricate with recommended lubricant at intervals noted on fan nameplate.
4 | Check integrity of electrical insulation | 6m | Check for soundness and ensure terminal connects are secure.
5 | Impeller | 6m | Check that there is no excessive movement at the wing root and inspect for any indent marks.
6 | Check the noise level | 6m | Inspect for abnormal noise level with DB meter
7 | Check the Fan vibration level | 6m | Inspect the vibration level with vibration meter
8 | Operate from MCC | 12m | operate the fans in manual mode in the MCC panels
9 | check the working of emergency stop botton | 6m | working/not
10 | Inspect the blade tips clearance | 6m | ensure for tip clearance as per standard
11 | Condition of vibration isolater | 6m | Inspect the vibration isolator legs with sprit level for evenness
12 | Check the flexible connector | 3m | Check for any damage postion of the flexible connect and rectify
13 | Check the elctrical termination in the Fan and Motor | 3m | inspect for any loose connection if nessecary tighten or recrimp it
14 | Physical Inspection | Weekly | Physical inspection of all equipment for any signs of noise/vibration/electrical wiring and connection.
B) DAMPERS
S. No | Item | Frequency (Months) | Action
1 | Actuator | 3m | Check for cam setting
2 | Clean Blades | 3m | Clean dust and entrapment of foreign particles
3 | Check Linkages | 3m | Check for smooth movement and cotter pin to be intact
4 | Manual close/open | 3m | open/close manually and check for actuator spring tightness
5 | Frame | 3m | Check for corrosion, re-paint/touch up as required and Tightness of Nut & Bolt
6 | Actuator wiring | 3m | Physical inspection
7 | Rattling sound while close/open | 3m | Physical inspection
8 | Blade alignment | 3m | Inspect the blades in close and open position
9 | Function of limit switch | 3m | Check for limit switch signal
10 | Physical Inspection | Weekly | Physical inspection of all equipment for any signs of noise/vibration/electrical wiring and connection.